## Slide 1: Water Main Replacement Analysis Results August 28, 2018

## Slide 2: Water Main Replacement Prioritization Study Goals
Develop tool for focused replacement based on condition, not age
Provide basis for determining future budgets based on service level goals
Establish metric-driven capital improvement plan based on risk (likelihood and consequence of main failures)
Form collaborative approach with Public Works for mutually beneficial projects

## Slide 3: Main Break Analysis
01
Notes: To hit those goals, need to dive into the break history and data

## Slide 4: RPU System
Growing system:
  Grown from under 300 miles in 1988 to currently ~600 miles
Low break rate (or number of breaks per 100 miles)
  Approximately 8 (5-year average)
Pipe diameters in the RPU system range from 0.75 to 24 inches

## Slide 5
Historical Water Main Break Summary: 1988-2016
Miles of Water Main
Water Main Breaks / 100 Miles of Water Main
Notes: At system level, break rate looks relatively flat

## Slide 6
Anticipated Annual water main replacement schedule
Feet of Pipe to be Replaced Per Year
Replacement Years
Notes: If you look at the problem simply from a age based replacement, there is a coming “wave” of replacement needs.
This is typical for a number of facilities.
To make sure RPU gets highest ROI, we look at this from a risk perspective.

## Slide 7: Main Break Analysis
Potential primary and secondary drivers of water main deterioration
  Material Vintage (age and material)
  Diameter
  Soil Data (Shrink/Swell, Steel Corrosion, & Frost Heave)
  Pressure
  Number of Taps
Proposed groupings, or cohorts, based on analysis of RPU data
Notes: Risk-based; not age based

## Slide 8
Notes: If replacement is based purely on age, there is a significant difference in performance. For example, CIP installed in 1918 (on average) has a break rate of under 5 as compared to CIP installed in 1958 with a break rate of over 30.

## Slide 9: Benchmarking
02

## Slide 10
Notes: Ahead of the AWWA goal, but want to stay there

## Slide 11: Break Forecast
03

## Slide 12: Baseline – Replacements Sorted By Age
Break Rate = 23
  5-year average for 2039-2043
  Almost 200% increase over existing
Notes: All the forecasts are based on the break history; more breaks increase

## Slide 13: Prioritizing Investments – Assumes 100% Eff.
Same amount (i.e. length) of annual replacement
Break rate = 10
  ~23% increase over existing
Potential Value of Risk Prioritization
Notes: Providing better “customer service” for same investments
Doug to insert

## Slide 14: Scenario A – Business as Usual
Key Assumptions – Scenario A
5,700 ft/yr – initial renewal level
0% - annual increase in renewal level
75% - effectiveness of replacement
Notes: Last five years vs 2017

## Slide 15: Scenario B – Maintain Existing Service Levels
Key Assumptions – Scenario B
7,500 ft/yr – initial renewal level
5% - annual increase in renewal level
75% - effectiveness of replacement

## Slide 16: Scenario C – Improve Service Levels
Key Assumptions – Scenario C
12,000 ft/yr – initial renewal level
3.5% - annual increase in renewal level
75% - effectiveness of replacement

## Slide 17: Next Steps
04

## Slide 18: Next Steps
Phase 1 – Break Data and Service Level Analysis including Likelihood of Failure (LoF) Analysis
  Completed 2nd Quarter 2018
Phase 2 – Risk Prioritization (LoF and Consequence of Failure Analysis)
  Complete Early 1st Quarter 2019
Phase 3 – Capital Improvement Planning
  Complete Late 1st Quarter 2019
Notes: Doug is going to cover this.

## Slide 19: Questions?

## Slide 20: Benchmarking Survey Results
Reference Utility | System Length, mi | Break Rate1 | Current Length Replaced1, mi | Replacement Ratio
Rochester Public Utilities | 578 | 8 | 1.1 | 0.19%
City of Minneapolis Water | 1,100 | 30 | 2.8 | 0.25%
Des Moines Water Works | 1,441 | 22 | 6.8 | 0.47%
Lincoln Water System | 1,225 | 10 | 7.0 | 0.57%
Metropolitan Utilities District | 2,928 | 17 | 11.0 | 0.38%
St. Paul Regional Water Services | 1,185 | 11 | 8.0 | 0.68%
City of St. Cloud | 302 | 2 | 1.7 | 0.57%
City of Sioux Falls | 1,056 | 3 | 12.0 | 1.14%
City of Cedar Rapids | 671 | 15 | 2.6 | 0.39%
City of Mankato | 257 | 9 | 0.7 | 0.26%
Notes: Communities of similar or larger size; older systems; core with a lot of development
Not “peer”; Upper Midwest communities

## Slide 21: Break Forecast – 3 Components

## Slide 22
Chart: Age
Miles of Active Pipe | 494.0443 | 3453.228 | 3473.7703 | 2613.3353 | 2038.3373 | 1626.3892 | 1336.2895 | 1087.0115 | 832.2735 | 554.4446 | 374.2975 | 273.7849 | 260.9466 | 206.4437 | 137.0259 | 93.9731 | 58.0773 | 48.7177 | 41.8951 | 18.3679
 | 2.2265 | 0.52125 | 1.1227 | 2.5638 | 7.1627 | 11.0675 | 13.6198 | 17.8471 | 19.7051 | 18.3968 | 11.4882 | 4.7483 | 9.5805 | 5.8127 | 6.5681 | 3.1924 | 17.2184 | 2.0526 | 11.9346 | 0
Notes: Need to explain explicitly what each of these are.

## Slide 25: Main Break Analysis - Results
Primary and secondary drivers of deterioration determined by analysis
  Material Vintage (age and material) - Primary
  Diameter - secondary
  Soil Data (Shrink/swell, Steel Corrosion, & Frost Heave) - secondary
  Number of Taps
  Pressure
These factors will be used in prioritization (Phase 2)